## EDE
# Proposal_Engineering-Data-Exchange - B.I.G.-EU
PROJECT_NAME | EDE DK-AC-BAC1
VERSION_OF_REFERENCEFILE | 3
TIMESTAMP_OF_LAST_CHANGE | 2018-06-26
AUTHOR_OF_LAST_CHANGE | csole
VERSION_OF_LAYOUT | 1.0.0.0
#mandatory | mandatory | mandatory | mandatory | mandatory | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional
# keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | settable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-address
DK-AC-BAC-1 | 246000 | DK-AC-BAC-1 | 8 | 246000 | Daikin AC interface |  |  |  | N | N
OnOff_status | 246000 | OnOff_status | 3 | 0 |  |  |  |  | N | Y |  |  | 0
OnOff_command | 246000 | OnOff_command | 4 | 0 |  |  |  |  | Y | Y |  |  | 0
Mode_status | 246000 | Mode_status | 13 | 0 |  |  |  |  | N | Y |  |  | 1
Mode_command | 246000 | Mode_command | 14 | 0 |  |  |  |  | Y | Y |  |  | 2
SetPoint_status | 246000 | SetPoint_status | 0 | 0 |  |  | 10 | 32 | N | Y |  |  |  | 62
SetPoint_command | 246000 | SetPoint_command | 1 | 0 |  |  | 10 | 32 | Y | Y |  |  |  | 62
FanSpeed_status | 246000 | FanSpeed_status | 13 | 1 |  |  |  |  | N | Y |  |  | 3
FanSpeed_command | 246000 | FanSpeed_command | 14 | 1 |  |  |  |  | Y | Y |  |  | 3
AirDirectionUD_status | 246000 | AirDirectionUD_status | 13 | 2 |  |  |  |  | N | Y |  |  | 4
AirDirectionUD_command | 246000 | AirDirectionUD_command | 14 | 2 |  |  |  |  | Y | Y |  |  | 4
AirDirectionLR_status | 246000 | AirDirectionLR_status | 13 | 3 |  |  |  |  | N | Y |  |  | 4
AirDirectionLR_command | 246000 | AirDirectionLR_command | 14 | 3 |  |  |  |  | Y | Y |  |  | 4
RoomTemperature_status | 246000 | RoomTemperature_status | 0 | 1 |  |  |  |  | N | Y |  |  |  | 62
ErrorCode | 246000 | ErrorCode | 0 | 2 |  |  |  |  | N | Y
ErrorCodeM | 246000 | ErrorCodeM | 13 | 4 |  |  |  |  | N | Y |  |  | 5
ErrorActive | 246000 | ErrorActive | 3 | 1 |  |  |  |  | N | Y |  |  | 6
OnTimeCounter | 246000 | OnTimeCounter | 2 | 0 |  |  |  |  | Y | Y |  |  |  | 71
Occupancy | 246000 | Occupancy | 19 | 0 |  |  |  |  | Y | Y |  |  | 9
OccupiedCoolSetPoint | 246000 | OccupiedCoolSetPoint | 2 | 1 |  |  |  |  | Y | Y |  |  |  | 62
OccupiedHeatSetPoint | 246000 | OccupiedHeatSetPoint | 2 | 2 |  |  |  |  | Y | Y |  |  |  | 62
UnoccupiedCoolSetPoint | 246000 | UnoccupiedCoolSetPoint | 2 | 3 |  |  |  |  | Y | Y |  |  |  | 62
UnoccupiedHeatSetPoint | 246000 | UnoccupiedHeatSetPoint | 2 | 4 |  |  |  |  | Y | Y |  |  |  | 62
OccupancyContinuousCheck | 246000 | OccupancyContinuousCheck | 5 | 0 |  |  |  |  | Y | Y |  |  | 10
UnoccupiedDeadbandAction | 246000 | UnoccupiedDeadbandAction | 5 | 1 |  |  |  |  | Y | Y |  |  | 11
LockRemoteControl | 246000 | LockRemoteControl | 5 | 2 |  |  |  |  | Y | Y |  |  | 7
Humidification_status | 246000 | Humidification_status | 13 | 8 |  |  |  |  | N | Y |  |  | 8
Humidification_command | 246000 | Humidification_command | 14 | 6 |  |  |  |  | Y | Y |  |  | 8
OutdoorTemp_status | 246000 | OutdoorTemp_status | 0 | 8 |  |  |  |  | N | Y |  |  |  | 62
#NOTE: Default device instance is 246000 + SW2 selected address (MAC MS/TP address)
#NOTE: The unit-code 62 can be changed to 64 with switch SW3 P5

## State-Texts
#State Text Reference
#Reference Number | Text 1 or Inactive-Text | Text 2 or Active-Text | Text 3 | Text 4 | Text 5 | Text 6 | Text 7 | Text 8 | Text 9 | Text 10 | Text 11 | Text 12 | Text 13 | Text 14 | Text 15 | Text 16 | Text 17 | Text 18 | Text 19 | Text 20 | Text 21 | Text 22 | Text 23 | Text 24 | Text 25 | Text 26 | Text 27 | Text 28 | Text 29 | Text 30 | Text 31 | Text 32 | Text 33 | Text 34 | Text 35 | Text 36 | Text 37 | Text 38 | Text 39 | Text 40 | Text 41 | Text 42 | Text 43 | Text 44 | Text 45 | Text 46 | Text 47 | Text 48 | Text 49 | Text 50 | Text 51 | Text 52 | Text 53 | Text 54 | Text 55 | Text 56 | Text 57 | Text 58 | Text 59 | Text 60 | Text 61 | Text 62 | Text 63 | Text 64 | Text 65 | Text 66 | Text 67 | Text 68 | Text 69 | Text 70 | Text 71 | Text 72 | Text 73 | Text 74 | Text 75 | Text 76 | Text 77 | Text 78 | Text 79 | Text 80 | Text 81 | Text 82 | Text 83 | Text 84 | Text 85 | Text 86 | Text 87 | Text 88 | Text 89 | Text 90 | Text 91 | Text 92 | Text 93 | Text 94 | Text 95 | Text 96 | Text 97 | Text 98 | Text 99 | Text 100 | Text 101 | Text 102 | Text 103 | Text 104 | Text 105 | Text 106 | Text 107 | Text 108 | Text 109 | Text 110 | Text 111 | Text 112 | Text 113 | Text 114 | Text 115 | Text 116 | Text 117 | Text 118 | Text 119 | Text 120 | Text 121 | Text 122 | Text 123 | Text 124 | Text 125 | Text 126 | Text 127 | Text 128 | Text 129 | Text 130 | Text 131 | Text 132 | Text 133 | Text 134 | Text 135 | Text 136 | Text 137 | Text 138 | Text 139 | Text 140 | Text 141 | Text 142 | Text 143 | Text 144 | Text 145 | Text 146 | Text 147 | Text 148 | Text 149 | Text 150 | Text 151 | Text 152 | Text 153 | Text 154 | Text 155 | Text 156
0 | Off | On
1 | Heat | Cool | Text 3: Fan; Text 4: Dry; Text 5: Auto; Text 6: AutoHeat; Text 7: AutoCool
2 | Heat | Cool | Text 3: Fan; Text 4: Dry; Text 5: Auto
3 | Auto | Fan Speed 1 | Text 3: Fan Speed 2; Text 4: Fan Speed 3; Text 5: Fan Speed 4; Text 6: Fan Speed 5
4 | Stop | Swing
5 |  | CommError | A0 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | A9 | AA | AH | AJ | AE | AF | C0 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | CA | CH | CC | CJ | CE | CF | E0 | E1 | E3 | E4 | E5 | E6 | E7 | E8 | E9 | EA | EH | EC | EJ | EE | EF | H0 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8 | H9 | HA | HH | HC | HE | HF | F0 | F1 | F2 | F3 | F6 | FA | FH | FC | FE | FF | J0 | J1 | J2 | J3 | J4 | J5 | J6 | J7 | J8 | J9 | JA | JH | JC | JE | JF | L0 | L3 | L4 | L5 | L6 | L7 | L8 | L9 | LA | LC | P0 | P1 | P3 | P4 | P5 | P6 | P7 | PJ | U0 | U1 | U2 | U3 | U4 | U5 | U6 | U7 | U8 | U9 | UA | UH | UC | UJ | UE | UF | 60 | 61 | 62 | 63 | 64 | 65 | 68 | 6A | 6H | 6C | 6J | 6E | 6F | 51 | 52 | 53 | 54 | 40 | 41 | 42 | 43 | 44 | 31 | 32 | 33 | 34 | 35 | 36 | 3A | 3H | 3C | M2 | M8 | MA | MC | UNKNOWN
6 | No | Error
7 | Unlocked | Locked
8 | Off | Low | Text 3: Mid; Text 4: High; Text 5: Continuous
9 | Occupied | Unoccupied | Text 3: Disabled
10 | Disabled | Enabled
11 | Off | CurrentMode

## Unit-Texts
#Encoding of BACnet Engineering Units
#Code | Unit Text
62 | DEGREES-CELSIUS
64 | DEGREES-FAHRENHEIT
71 | HOURS

## Object-Types
#Encoding of BACnet Object Types
#Code | Object Type
0 | Analog Input
1 | Analog Output
2 | Analog Value
3 | Binary Input
4 | Binary Output
5 | Binary Value
8 | Device
13 | Multistate Input
14 | Multistate Output