## EDE
# Proposal_Engineering-Data-Exchange - B.I.G.-EU
PROJECT_NAME | EDE ME-AC-BAC-1L
VERSION_OF_REFERENCEFILE | 1
TIMESTAMP_OF_LAST_CHANGE | 2018-10-25
AUTHOR_OF_LAST_CHANGE | csole
VERSION_OF_LAYOUT | 1.0.0.0
#mandatory | mandatory | mandatory | mandatory | mandatory | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional
# keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | settable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-address
ME-AC-BAC-1 | 246000 | ME-AC-BAC-1 | 8 | 246000 | Mitsubishi Electric AC interface |  |  |  | N | N
OnOff_status | 246000 | OnOff_status | 3 | 0 |  |  |  |  | N | Y |  |  | 0
OnOff_command | 246000 | OnOff_command | 4 | 0 |  |  |  |  | Y | Y |  |  | 0
Mode_status | 246000 | Mode_status | 13 | 0 |  |  |  |  | N | Y |  |  | 1
Mode_command | 246000 | Mode_command | 14 | 0 |  |  |  |  | Y | Y |  |  | 1
SetPoint_status | 246000 | SetPoint_status | 0 | 0 |  |  | 16 or 61 | 31 or 89 | N | Y |  |  |  | 62
SetPoint_command | 246000 | SetPoint_command | 1 | 0 |  |  | 16 or 61 | 31 or 89 | Y | Y |  |  |  | 62
FanSpeed_status | 246000 | FanSpeed_status | 13 | 1 |  |  |  |  | N | Y |  |  | 2
FanSpeed_command | 246000 | FanSpeed_command | 14 | 1 |  |  |  |  | Y | Y |  |  | 2
AirDirectionUD_status | 246000 | AirDirectionUD_status | 13 | 2 |  |  |  |  | N | Y |  |  | 3
AirDirectionUD_command | 246000 | AirDirectionUD_command | 14 | 2 |  |  |  |  | Y | Y |  |  | 3
RoomTemperature_status | 246000 | RoomTemperature_status | 0 | 1 |  |  |  |  | N | Y |  |  |  | 62
RoomTemperature_command | 246000 | RoomTemperature_command | 1 | 1 |  |  |  |  | N | Y |  |  |  | 62
ErrorCode | 246000 | ErrorCode | 0 | 2 |  |  |  |  | N | Y
ErrorCodeM | 246000 | ErrorCodeM | 13 | 4 |  |  |  |  | N | Y |  |  | 4
ErrorActive | 246000 | ErrorActive | 3 | 1 |  |  |  |  | Y | Y |  |  | 5
OnTimeCounter | 246000 | OnTimeCounter | 2 | 0 |  |  |  |  | Y | Y |  |  |  | 71
Occupancy | 246000 | Occupancy | 19 | 0 |  |  |  |  | Y | Y |  |  | 6
OccupiedCoolSetPoint | 246000 | OccupiedCoolSetPoint | 2 | 1 |  |  |  |  | Y | Y |  |  |  | 62
OccupiedHeatSetPoint | 246000 | OccupiedHeatSetPoint | 2 | 2 |  |  |  |  | Y | Y |  |  |  | 62
UnoccupiedCoolSetPoint | 246000 | UnoccupiedCoolSetPoint | 2 | 3 |  |  |  |  | Y | Y |  |  |  | 62
UnoccupiedHeatSetPoint | 246000 | UnoccupiedHeatSetPoint | 2 | 4 |  |  |  |  | Y | Y |  |  |  | 62
OccupancyContinuousCheck | 246000 | OccupancyContinuousCheck | 5 | 0 |  |  |  |  | Y | Y |  |  | 7
UnoccupiedDeadbandAction | 246000 | UnoccupiedDeadbandAction | 5 | 1 |  |  |  |  | Y | Y |  |  | 8
LockRemoteControl | 246000 | LockRemoteControl | 5 | 2 |  |  |  |  | N | Y |  |  | 9
DIP_SW_S1_status | 246000 | DIP_SW_S1_status | 0 | 9 |  |  |  |  | N | Y
DIP_SW_S2_status | 246000 | DIP_SW_S2_status | 0 | 10 |  |  |  |  | N | Y
SerialNumber | 246000 | SerialNumber | 0 | 11 |  |  |  |  | N | Y
#NOTE: Default device instance is 246000 + SW2 selected address (MAC MS/TP address)
#NOTE: The unit-code 62 can be changed to 64 with switch SW2 P8

## State-Texts
#State Text Reference
#Reference Number | Text 1 or Inactive-Text | Text 2 or Active-Text | Text 3 | Text 4 | Text 5 | Text 6 | Text 7 | Text 8 | Text 9 | Text 10 | Text 11 | Text 12 | Text 13 | Text 14 | Text 15 | Text 16 | Text 17 | Text 18 | Text 19 | Text 20 | Text 21 | Text 22 | Text 23 | Text 24 | Text 25 | Text 26 | Text 27 | Text 28 | Text 29 | Text 30 | Text 31 | Text 32 | Text 33 | Text 34 | Text 35 | Text 36 | Text 37 | Text 38 | Text 39 | Text 40 | Text 41 | Text 42 | Text 43 | Text 44 | Text 45 | Text 46 | Text 47 | Text 48
0 | Off | On
1 | Heat | Cool | Text 3: Fan; Text 4: Dry; Text 5: Auto
2 | Auto | Fan Speed 1 | Text 3: Fan Speed 2; Text 4: Fan Speed 3; Text 5: Fan Speed 4
3 | Auto | Up | Text 3: Mid-1; Text 4: Mid-2; Text 5: Mid-3; Text 6: Down; Text 7: Swing
4 |  | CommError | 1102 | 1108 | 1110 | 1300 | 1302 | 1503 | 1504 | 1509 | 1520 | 2500 | 2502 | 2503 | 4030 | 4100 | 4101 | 4102 | 4103 | 4108 | 4118 | 4124 | 4210 | 4220 | 4230 | 5101 | 5102 | 5104 | 5105 | 5106 | 5107 | 5110 | 5202 | 5300 | 6600 | 6602 | 6603 | 6606 | 6607 | 6608 | 6831 | 6832 | 6840 | 6841 | 6844 | 6845 | 6846 | UNKNOWN
5 | No | Error
6 | Occupied | Unoccupied | Text 3: Disabled
7 | Disabled | Enabled
8 | Off | CurrentMode
9 | Unlocked | Locked
10 | Non Active | Active

## Unit-Texts
#Encoding of BACnet Engineering Units
#Code | Unit Text
62 | DEGREES-CELSIUS
64 | DEGREES-FAHRENHEIT
71 | HOURS

## Object-Types
#Encoding of BACnet Object Types
#Code | Object Type
0 | Analog Input
1 | Analog Output
2 | Analog Value
3 | Binary Input
4 | Binary Output
5 | Binary Value
8 | Device
13 | Multistate Input
14 | Multistate Output
19 | Multistate Value