## EDE
# Proposal_Engineering-Data-Exchange - B.I.G.-EU
PROJECT_NAME | EDE PA-AC-BAC1
VERSION_OF_REFERENCEFILE | 2
TIMESTAMP_OF_LAST_CHANGE | 2018-05-08
AUTHOR_OF_LAST_CHANGE | csole
VERSION_OF_LAYOUT | 1.0.0.0
#mandatory | mandatory | mandatory | mandatory | mandatory | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional
# keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | settable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-address
PA-AC-BAC-1 | 246000 | PA-AC-BAC-1 | 8 | 246000 | Panasonic AC interface |  |  |  | N | N
OnOff_status | 246000 | OnOff_status | 3 | 0 |  |  |  |  | N | Y |  |  | 0
OnOff_command | 246000 | OnOff_command | 4 | 0 |  |  |  |  | Y | Y |  |  | 0
Mode_status | 246000 | Mode_status | 13 | 0 |  |  |  |  | N | Y |  |  | 1
Mode_command | 246000 | Mode_command | 14 | 0 |  |  |  |  | Y | Y |  |  | 2
SetPoint_status | 246000 | SetPoint_status | 0 | 0 |  |  | 16 or 8 | 30 or 10 | N | Y |  |  |  | 62
SetPoint_command | 246000 | SetPoint_command | 1 | 0 |  |  | 16 or 8 | 30 or 10 | Y | Y |  |  |  | 62
FanSpeed_status | 246000 | FanSpeed_status | 13 | 1 |  |  |  |  | N | Y |  |  | 3
FanSpeed_command | 246000 | FanSpeed_command | 14 | 1 |  |  |  |  | Y | Y |  |  | 3
AirDirectionUD_status | 246000 | AirDirectionUD_status | 13 | 2 |  |  |  |  | N | Y |  |  | 4
AirDirectionUD_command | 246000 | AirDirectionUD_command | 14 | 2 |  |  |  |  | Y | Y |  |  | 4
AirDirectionLR_status | 246000 | AirDirectionLR_status | 13 | 3 |  |  |  |  | N | Y |  |  | 5
AirDirectionLR_command | 246000 | AirDirectionLR_command | 14 | 3 |  |  |  |  | Y | Y |  |  | 5
RoomTemperature_status | 246000 | RoomTemperature_status | 0 | 1 |  |  |  |  | N | Y |  |  |  | 62
ErrorCode | 246000 | ErrorCode | 0 | 2 |  |  |  |  | N | Y
ErrorCodeM | 246000 | ErrorCodeM | 13 | 4 |  |  |  |  | N | Y |  |  | 6
ErrorActive | 246000 | ErrorActive | 3 | 1 |  |  |  |  | N | Y |  |  | 7
OnTimeCounter | 246000 | OnTimeCounter | 2 | 0 |  |  |  |  | Y | Y |  |  |  | 71
PowerConsumption | 246000 | PowerConsumption | 0 | 3 |  |  |  |  | N | Y |  |  |  | 47
Occupancy | 246000 | Occupancy | 19 | 0 |  |  |  |  | Y | Y |  |  | 8
OccupiedCoolSetPoint | 246000 | OccupiedCoolSetPoint | 2 | 1 |  |  |  |  | Y | Y |  |  |  | 62
OccupiedHeatSetPoint | 246000 | OccupiedHeatSetPoint | 2 | 2 |  |  |  |  | Y | Y |  |  |  | 62
UnoccupiedCoolSetPoint | 246000 | UnoccupiedCoolSetPoint | 2 | 3 |  |  |  |  | Y | Y |  |  |  | 62
UnoccupiedHeatSetPoint | 246000 | UnoccupiedHeatSetPoint | 2 | 4 |  |  |  |  | Y | Y |  |  |  | 62
OccupancyContinuousCheck | 246000 | OccupancyContinuousCheck | 5 | 0 |  |  |  |  | Y | Y |  |  | 9
UnoccupiedDeadbandAction | 246000 | UnoccupiedDeadbandAction | 5 | 1 |  |  |  |  | Y | Y |  |  | 10
LockRemoteControl | 246000 | LockRemoteControl | 5 | 2 |  |  |  |  | Y | Y |  |  | 11
Powerful_status | 246000 | Powerful_status | 3 | 2 |  |  |  |  | N | Y |  |  | 0
Powerful_command | 246000 | Powerful_command | 4 | 1 |  |  |  |  | Y | Y |  |  | 0
Quiet_status | 246000 | Quiet_status | 3 | 3 |  |  |  |  | N | Y |  |  | 0
Quiet_command | 246000 | Quiet_command | 4 | 2 |  |  |  |  | Y | Y |  |  | 0
RoomFreezeProtection_status | 246000 | RoomFreezeProtection_status | 3 | 4 |  |  |  |  | N | Y |  |  | 0
RoomFreezeProtection_command | 246000 | RoomFreezeProtection_command | 4 | 3 |  |  |  |  | Y | Y |  |  | 0
EcoMode_status | 246000 | EcoMode_status | 13 | 5 |  |  |  |  | N | Y |  |  | 12
EcoMode_command | 246000 | EcoMode_command | 14 | 4 |  |  |  |  | Y | Y |  |  | 12
HumanActivity | 246000 | HumanActivity | 3 | 5 |  |  |  |  | N | Y |  |  | 13
OutdoorTemperature_status | 246000 | OutdoorTemperature_status | 0 | 8 |  |  |  |  | N | Y |  |  |  | 62
AccumulatedEnergy | 246000 | AccumulatedEnergy | 2 | 5 |  |  |  |  | Y | Y |  |  |  | 18
#NOTE: Default device instance is 246000 + SW2 selected address (MAC MS/TP address)
#NOTE: The unit-code 62 can be changed to 64 with switch SW3 P5

## State-Texts
#State Text Reference
#Reference Number | Text 1 or Inactive-Text | Text 2 or Active-Text | Text 3 | Text 4 | Text 5 | Text 6 | Text 7 | Text 8 | Text 9 | Text 10 | Text 11 | Text 12 | Text 13 | Text 14 | Text 15 | Text 16 | Text 17 | Text 18 | Text 19 | Text 20 | Text 21 | Text 22 | Text 23 | Text 24 | Text 25 | Text 26 | Text 27 | Text 28 | Text 29 | Text 30 | Text 31 | Text 32 | Text 33 | Text 34 | Text 35 | Text 36 | Text 37 | Text 38 | Text 39 | Text 40 | Text 41 | Text 42 | Text 43 | Text 44 | Text 45 | Text 46 | Text 47 | Text 48 | Text 49 | Text 50 | Text 51 | Text 52 | Text 53 | Text 54 | Text 55 | Text 56 | Text 57 | Text 58 | Text 59 | Text 60 | Text 61 | Text 62 | Text 63 | Text 64 | Text 65 | Text 66 | Text 67 | Text 68 | Text 69 | Text 70 | Text 71 | Text 72 | Text 73 | Text 74 | Text 75 | Text 76 | Text 77 | Text 78 | Text 79 | Text 80 | Text 81 | Text 82 | Text 83 | Text 84 | Text 85 | Text 86 | Text 87 | Text 88 | Text 89 | Text 90 | Text 91 | Text 92 | Text 93 | Text 94 | Text 95 | Text 96 | Text 97 | Text 98 | Text 99 | Text 100 | Text 101 | Text 102 | Text 103 | Text 104 | Text 105 | Text 106 | Text 107 | Text 108 | Text 109 | Text 110 | Text 111 | Text 112 | Text 113 | Text 114 | Text 115 | Text 116 | Text 117 | Text 118 | Text 119 | Text 120 | Text 121 | Text 122 | Text 123 | Text 124 | Text 125 | Text 126 | Text 127 | Text 128 | Text 129 | Text 130 | Text 131 | Text 132 | Text 133 | Text 134 | Text 135 | Text 136 | Text 137 | Text 138 | Text 139 | Text 140 | Text 141 | Text 142 | Text 143 | Text 144 | Text 145 | Text 146 | Text 147 | Text 148 | Text 149 | Text 150 | Text 151 | Text 152 | Text 153 | Text 154 | Text 155 | Text 156 | Text 157 | Text 158 | Text 159 | Text 160 | Text 161 | Text 162 | Text 163 | Text 164 | Text 165 | Text 166 | Text 167 | Text 168 | Text 169 | Text 170 | Text 171 | Text 172 | Text 173 | Text 174 | Text 175 | Text 176 | Text 177 | Text 178 | Text 179 | Text 180 | Text 181 | Text 182 | Text 183 | Text 184 | Text 185 | Text 186 | Text 187 | Text 188 | Text 189 | Text 190 | Text 191 | Text 192 | Text 193 | Text 194 | Text 195 | Text 196 | Text 197 | Text 198 | Text 199 | Text 200 | Text 201 | Text 202 | Text 203 | Text 204 | Text 205 | Text 206 | Text 207 | Text 208 | Text 209 | Text 210 | Text 211 | Text 212 | Text 213 | Text 214 | Text 215 | Text 216 | Text 217 | Text 218 | Text 219 | Text 220 | Text 221 | Text 222 | Text 223 | Text 224 | Text 225 | Text 226 | Text 227 | Text 228 | Text 229 | Text 230 | Text 231 | Text 232 | Text 233 | Text 234 | Text 235 | Text 236 | Text 237 | Text 238 | Text 239 | Text 240 | Text 241 | Text 242 | Text 243 | Text 244 | Text 245 | Text 246 | Text 247 | Text 248 | Text 249 | Text 250 | Text 251 | Text 252 | Text 253 | Text 254 | Text 255 | Text 256 | Text 257 | Text 258 | Text 259
0 | Off | On
1 | Heat | Cool | Text 3: Fan; Text 4: Dry; Text 5: Auto; Text 6: AutoHeat; Text 7: AutoCool
2 | Heat | Cool | Text 3: Fan; Text 4: Dry; Text 5: Auto
3 | Auto | Fan Speed 1 | Text 3: Fan Speed 2; Text 4: Fan Speed 3; Text 5: Fan Speed 4; Text 6: Fan Speed 5
4 | Auto | Up | Text 3: Mid-1; Text 4: Mid-2; Text 5: Mid-3; Text 6: Down
5 | Auto | Left | Text 3: Mid-1; Text 4: Mid-2; Text 5: Mid-3; Text 6: Right
6 |  | CommError | Text 3: H11; Text 4: H12; Text 5: H14; Text 6: H15; Text 7: H16; Text 8: H19; Text 9: H23; Text 10: H25; Text 11: H27; Text 12: H28; Text 13: H30; Text 14: H32; Text 15: H33; Text 16: H34; Text 17: H36; Text 18: H37; Text 19: H38; Text 20: H39; Text 21: H41; Text 22: H58; Text 23: H59; Text 24: H64; Text 25: H97; Text 26: H98; Text 27: H99; Text 28: F11; Text 29: F17; Text 30: F90; Text 31: F91; Text 32: F93; Text 33: F94; Text 34: F95; Text 35: F96; Text 36: F97; Text 37: F98; Text 38: F99; Text 39: UNKNOWN
7 | No | Error
8 | Occupied | Unoccupied | Text 3: Disabled
9 | Disabled | Enabled
10 | Off | CurrentMode
11 | Unlocked | Locked
12 | Off | ECONAVI | Text 3: AutoConfort
13 | No | Yes

## Unit-Texts
#Encoding of BACnet Engineering Units
#Code | Unit Text
62 | DEGREES-CELSIUS
64 | DEGREES-FAHRENHEIT
47 | WATTS
71 | HOURS
18 | WATT-HOUR

## Object-Types
#Encoding of BACnet Object Types
#Code | Object Type
0 | Analog Input
1 | Analog Output
2 | Analog Value
3 | Binary Input
4 | Binary Output
5 | Binary Value
8 | Device
13 | Multistate Input
14 | Multistate Output
19 | Multistate Value